## T322AI
ID | Register_Address | Operation | Register_Length | Register_Name | Data_Format | Description
1 | 0 | 03 Read Holding Registers (4x) | 4 | MODBUS_SERIALNUMBER | 32 Bit Unsigned Integer LO_HI | serial numbler
2 | 4 | 03 Read Holding Registers (4x) | 2 | MODBUS_FIRMWARE_VERSION | 16 Bit Unsigned Integer | firmware Version
3 | 6 | 03_06 Read Holding and Write Single | 1 | MODBUS_ADDRESS | 8 Bit Unsigned Integer | Modbus device address
4 | 7 | 03 Read Holding Registers (4x) | 1 | MODBUS_PRODUCT_MODEL | 16 Bit Unsigned Integer | Prodouct model
5 | 8 | 03 Read Holding Registers (4x) | 1 | MODBUS_HARDWARE_REV | 16 Bit Unsigned Integer | Hardware Version Number
6 | 100 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE0_HI | 16 Bit Unsigned Integer | analog input 0 high byte
7 | 101 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE0_LO | 16 Bit Unsigned Integer | analog input 0 low byte
8 | 102 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE1_HI | 16 Bit Unsigned Integer | analog input 1 high byte
9 | 103 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE1_LO | 16 Bit Unsigned Integer | analog input 1 low byte
10 | 104 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE2_HI | 16 Bit Unsigned Integer | analog input 2 high byte
11 | 105 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE2_LO | 16 Bit Unsigned Integer | analog input 2 low byte
12 | 106 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE3_HI | 16 Bit Unsigned Integer | analog input 3 high byte
13 | 107 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE3_LO | 16 Bit Unsigned Integer | analog input 3 low byte
14 | 108 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE4_HI | 16 Bit Unsigned Integer | analog input 4 high byte
15 | 109 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE4_LO | 16 Bit Unsigned Integer | analog input 4 low byte
16 | 110 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE5_HI | 16 Bit Unsigned Integer | analog input 5 high byte
17 | 111 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE5_LO | 16 Bit Unsigned Integer | analog input 5 low byte
18 | 112 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE6_HI | 16 Bit Unsigned Integer | analog input 6 high byte
19 | 113 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE6_LO | 16 Bit Unsigned Integer | analog input 6 low byte
20 | 114 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE7_HI | 16 Bit Unsigned Integer | analog input 7 high byte
21 | 115 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE7_LO | 16 Bit Unsigned Integer | analog input 7 low byte
22 | 116 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE8_HI | 16 Bit Unsigned Integer | analog input 8 high byte
23 | 117 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE8_LO | 16 Bit Unsigned Integer | analog input 8 low byte
24 | 118 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE9_HI | 16 Bit Unsigned Integer | analog input 9 high byte
25 | 119 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE9_LO | 16 Bit Unsigned Integer | analog input 9 low byte
26 | 120 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE10_HI | 16 Bit Unsigned Integer | analog input 10 high byte
27 | 121 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE10_LO | 16 Bit Unsigned Integer | analog input 10 low byte
28 | 122 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE11_HI | 16 Bit Unsigned Integer | analog input 11 high byte
29 | 123 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE11_LO | 16 Bit Unsigned Integer | analog input 11 low byte
30 | 124 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE12_HI | 16 Bit Unsigned Integer | analog input 12 high byte
31 | 125 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE12_LO | 16 Bit Unsigned Integer | analog input 12 low byte
32 | 126 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE13_HI | 16 Bit Unsigned Integer | analog input 13 high byte
33 | 127 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE13_LO | 16 Bit Unsigned Integer | analog input 13 low byte
34 | 128 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE14_HI | 16 Bit Unsigned Integer | analog input 14 high byte
35 | 129 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE14_LO | 16 Bit Unsigned Integer | analog input 14 low byte
36 | 130 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE15_HI | 16 Bit Unsigned Integer | analog input 15 high byte
37 | 131 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE15_LO | 16 Bit Unsigned Integer | analog input 15 low byte
38 | 132 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE16_HI | 16 Bit Unsigned Integer | analog input 16 high byte
39 | 133 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE16_LO | 16 Bit Unsigned Integer | analog input 16 low byte
40 | 134 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE17_HI | 16 Bit Unsigned Integer | analog input 17 high byte
41 | 135 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE17_LO | 16 Bit Unsigned Integer | analog input 17 low byte
42 | 136 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE18_HI | 16 Bit Unsigned Integer | analog input 18 high byte
43 | 137 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE18_LO | 16 Bit Unsigned Integer | analog input 18 low byte
44 | 138 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE19_HI | 16 Bit Unsigned Integer | analog input 19 high byte
45 | 139 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE19_LO | 16 Bit Unsigned Integer | analog input 19 low byte
46 | 140 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE20_HI | 16 Bit Unsigned Integer | analog input 20 high byte
47 | 141 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE20_LO | 16 Bit Unsigned Integer | analog input 20 low byte
48 | 142 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE21_HI | 16 Bit Unsigned Integer | analog input 21 high byte
49 | 143 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE21_LO | 16 Bit Unsigned Integer | analog input 21 low byte
50 | 200 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER0 | 8 Bit Unsigned Integer | analog input 0 filter
51 | 201 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER1 | 8 Bit Unsigned Integer | analog input 1 filter
52 | 202 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER2 | 8 Bit Unsigned Integer | analog input 2 filter
53 | 203 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER3 | 8 Bit Unsigned Integer | analog input 3 filter
54 | 204 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER4 | 8 Bit Unsigned Integer | analog input 4 filter
55 | 205 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER5 | 8 Bit Unsigned Integer | analog input 5 filter
56 | 206 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER6 | 8 Bit Unsigned Integer | analog input 6 filter
57 | 207 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER7 | 8 Bit Unsigned Integer | analog input 7 filter
58 | 208 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER8 | 8 Bit Unsigned Integer | analog input 8 filter
59 | 209 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER9 | 8 Bit Unsigned Integer | analog input 9 filter
60 | 210 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER10 | 8 Bit Unsigned Integer | analog input 10 filter
61 | 211 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER11 | 8 Bit Unsigned Integer | analog input 11 filter
62 | 212 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER12 | 8 Bit Unsigned Integer | analog input 12 filter
63 | 213 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER13 | 8 Bit Unsigned Integer | analog input 13 filter
64 | 214 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER14 | 8 Bit Unsigned Integer | analog input 14 filter
65 | 215 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER15 | 8 Bit Unsigned Integer | analog input 15 filter
66 | 216 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER16 | 8 Bit Unsigned Integer | analog input 16 filter
67 | 217 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_FILTER17 | 8 Bit Unsigned Integer | analog input 17 filter
68 | 218 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER18 | 8 Bit Unsigned Integer | analog input 18 filter
69 | 219 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER19 | 8 Bit Unsigned Integer | analog input 19 filter
70 | 220 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER20 | 8 Bit Unsigned Integer | analog input 20 filter
71 | 221 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER21 | 8 Bit Unsigned Integer | analog input 21 filter
72 | 225 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE0 | 8 Bit Unsigned Integer | analog input 0 range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0_20m
73 | 226 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE1 | 8 Bit Unsigned Integer | analog input 1 range
74 | 227 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE2 | 8 Bit Unsigned Integer | analog input 2 range
75 | 228 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE3 | 8 Bit Unsigned Integer | analog input 3 range
76 | 229 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE4 | 8 Bit Unsigned Integer | analog input 4 range
77 | 230 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE5 | 8 Bit Unsigned Integer | analog input 5 range
78 | 231 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE6 | 8 Bit Unsigned Integer | analog input 6 range
79 | 232 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE7 | 8 Bit Unsigned Integer | analog input 7 range
80 | 233 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE8 | 8 Bit Unsigned Integer | analog input 8 range
81 | 234 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE9 | 8 Bit Unsigned Integer | analog input 9 range
82 | 235 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE10 | 8 Bit Unsigned Integer | analog input 10 range
83 | 236 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE11 | 8 Bit Unsigned Integer | analog input 11 range
84 | 237 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE12 | 8 Bit Unsigned Integer | analog input 12 range
85 | 238 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE13 | 8 Bit Unsigned Integer | analog input 13 range
86 | 239 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE14 | 8 Bit Unsigned Integer | analog input 14 range
87 | 240 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE15 | 8 Bit Unsigned Integer | analog input 15 range
88 | 241 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE16 | 8 Bit Unsigned Integer | analog input 16 range
89 | 242 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE17 | 8 Bit Unsigned Integer | analog input 17 range
90 | 243 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE18 | 8 Bit Unsigned Integer | analog input 18 range
91 | 244 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE19 | 8 Bit Unsigned Integer | analog input 19 range
92 | 245 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE20 | 8 Bit Unsigned Integer | analog input 20 range
93 | 246 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE21 | 8 Bit Unsigned Integer | analog input 21 range
94 | 247 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_0 | 8 Bit Unsigned Integer | auto manual setting for input 0
95 | 248 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_1 | 8 Bit Unsigned Integer | auto manual setting for input 1
96 | 249 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_2 | 8 Bit Unsigned Integer | auto manual setting for input 2
97 | 250 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_3 | 8 Bit Unsigned Integer | auto manual setting for input 3
98 | 251 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_4 | 8 Bit Unsigned Integer | auto manual setting for input 4
99 | 252 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_5 | 8 Bit Unsigned Integer | auto manual setting for input 5
100 | 253 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_6 | 8 Bit Unsigned Integer | auto manual setting for input 6
101 | 254 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_7 | 8 Bit Unsigned Integer | auto manual setting for input 7
102 | 255 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_8 | 8 Bit Unsigned Integer | auto manual setting for input 8
103 | 256 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_9 | 8 Bit Unsigned Integer | auto manual setting for input 9
104 | 257 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_10 | 8 Bit Unsigned Integer | auto manual setting for input 10
105 | 258 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_11 | 8 Bit Unsigned Integer | auto manual setting for input 11
106 | 259 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_12 | 8 Bit Unsigned Integer | auto manual setting for input 12
107 | 260 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_13 | 8 Bit Unsigned Integer | auto manual setting for input 13
108 | 261 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_14 | 8 Bit Unsigned Integer | auto manual setting for input 14
109 | 262 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_15 | 8 Bit Unsigned Integer | auto manual setting for input 15
110 | 263 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_16 | 8 Bit Unsigned Integer | auto manual setting for input 16
111 | 264 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_17 | 8 Bit Unsigned Integer | auto manual setting for input 17
112 | 265 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_18 | 8 Bit Unsigned Integer | auto manual setting for input 18
113 | 266 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_19 | 8 Bit Unsigned Integer | auto manual setting for input 19
114 | 267 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_20 | 8 Bit Unsigned Integer | auto manual setting for input 20
115 | 268 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_21 | 8 Bit Unsigned Integer | auto manual setting for input 21
116 | 269 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI0 | 8 Bit Unsigned Integer | digit and analog setting for input0 ( 0 - digital 1 - analog)
117 | 270 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI1 | 8 Bit Unsigned Integer | digit and analog setting for input1
118 | 271 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI2 | 8 Bit Unsigned Integer | digit and analog setting for input2
119 | 272 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI3 | 8 Bit Unsigned Integer | digit and analog setting for input3
120 | 273 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI4 | 8 Bit Unsigned Integer | digit and analog setting for input4
121 | 274 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI5 | 8 Bit Unsigned Integer | digit and analog setting for input5
122 | 275 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI6 | 8 Bit Unsigned Integer | digit and analog setting for input6
123 | 276 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI7 | 8 Bit Unsigned Integer | digit and analog setting for input7
124 | 277 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI8 | 8 Bit Unsigned Integer | digit and analog setting for input8
125 | 278 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI9 | 8 Bit Unsigned Integer | digit and analog setting for input9
126 | 279 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI10 | 8 Bit Unsigned Integer | digit and analog setting for input10
127 | 280 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI11 | 8 Bit Unsigned Integer | digit and analog setting for input11
128 | 281 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI12 | 8 Bit Unsigned Integer | digit and analog setting for input12
129 | 282 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI13 | 8 Bit Unsigned Integer | digit and analog setting for input13
130 | 283 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI14 | 8 Bit Unsigned Integer | digit and analog setting for input14
131 | 284 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI15 | 8 Bit Unsigned Integer | digit and analog setting for input15
132 | 285 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI16 | 8 Bit Unsigned Integer | digit and analog setting for input16
133 | 286 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI17 | 8 Bit Unsigned Integer | digit and analog setting for input17
134 | 287 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI18 | 8 Bit Unsigned Integer | digit and analog setting for input18
135 | 288 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI19 | 8 Bit Unsigned Integer | digit and analog setting for input19
136 | 289 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI20 | 8 Bit Unsigned Integer | digit and analog setting for input20
137 | 290 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI21 | 8 Bit Unsigned Integer | digit and analog setting for input21
138 | 291 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER0 | 8 Bit Unsigned Integer
139 | 292 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER1 | 8 Bit Unsigned Integer
140 | 293 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER2 | 8 Bit Unsigned Integer
141 | 294 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER3 | 8 Bit Unsigned Integer
142 | 295 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER4 | 8 Bit Unsigned Integer
143 | 296 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER5 | 8 Bit Unsigned Integer
144 | 297 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER6 | 8 Bit Unsigned Integer
145 | 298 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER7 | 8 Bit Unsigned Integer
146 | 299 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER8 | 8 Bit Unsigned Integer
147 | 300 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER9 | 8 Bit Unsigned Integer
148 | 301 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER10 | 8 Bit Unsigned Integer
149 | 302 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER11 | 8 Bit Unsigned Integer
150 | 303 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER12 | 8 Bit Unsigned Integer
151 | 304 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER13 | 8 Bit Unsigned Integer
152 | 305 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER14 | 8 Bit Unsigned Integer
153 | 306 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER15 | 8 Bit Unsigned Integer
154 | 307 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER16 | 8 Bit Unsigned Integer
155 | 308 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER17 | 8 Bit Unsigned Integer
156 | 309 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER18 | 8 Bit Unsigned Integer
157 | 310 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER19 | 8 Bit Unsigned Integer
158 | 311 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER20 | 8 Bit Unsigned Integer
159 | 312 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_JUPER21 | 8 Bit Unsigned Integer
160 | 313 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN0 | 8 Bit Unsigned Integer | Analog input calibration sign 0
161 | 314 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN1 | 8 Bit Unsigned Integer | Analog input calibration sign 1
162 | 315 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN2 | 8 Bit Unsigned Integer | Analog input calibration sign 2
163 | 316 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN3 | 8 Bit Unsigned Integer | Analog input calibration sign 3
164 | 317 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN4 | 8 Bit Unsigned Integer | Analog input calibration sign 4
165 | 318 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN5 | 8 Bit Unsigned Integer | Analog input calibration sign 5
166 | 319 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN6 | 8 Bit Unsigned Integer | Analog input calibration sign 6
167 | 320 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN7 | 8 Bit Unsigned Integer | Analog input calibration sign 7
168 | 321 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN8 | 8 Bit Unsigned Integer | Analog input calibration sign 8
169 | 322 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN9 | 8 Bit Unsigned Integer | Analog input calibration sign 9
170 | 323 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN10 | 8 Bit Unsigned Integer | Analog input calibration sign 10
171 | 324 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN11 | 8 Bit Unsigned Integer | Analog input calibration sign 11
172 | 325 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN12 | 8 Bit Unsigned Integer | Analog input calibration sign 12
173 | 326 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN13 | 8 Bit Unsigned Integer | Analog input calibration sign 13
174 | 327 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN14 | 8 Bit Unsigned Integer | Analog input calibration sign 14
175 | 328 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN15 | 8 Bit Unsigned Integer | Analog input calibration sign 15
176 | 329 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN16 | 8 Bit Unsigned Integer | Analog input calibration sign 16
177 | 330 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN17 | 8 Bit Unsigned Integer | Analog input calibration sign 17
178 | 331 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN18 | 8 Bit Unsigned Integer | Analog input calibration sign 18
179 | 332 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN19 | 8 Bit Unsigned Integer | Analog input calibration sign 19
180 | 333 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN20 | 8 Bit Unsigned Integer | Analog input calibration sign 20
181 | 334 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN21 | 8 Bit Unsigned Integer | Analog input calibration sign 21
182 | 335 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL0_HI | 16 Bit Unsigned Integer | calibrate value high byte input0
183 | 336 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL0_LO | 16 Bit Unsigned Integer | calibrate value low byte input0
184 | 337 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL1_HI | 16 Bit Unsigned Integer | calibrate value high byte input1
185 | 338 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL1_LO | 16 Bit Unsigned Integer | calibrate value low byte input1
186 | 339 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL2_HI | 16 Bit Unsigned Integer | calibrate value high byte input2
187 | 340 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL2_LO | 16 Bit Unsigned Integer | calibrate value low byte input2
188 | 341 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL3_HI | 16 Bit Unsigned Integer | calibrate value high byte input3
189 | 342 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL3_LO | 16 Bit Unsigned Integer | calibrate value low byte input3
190 | 343 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL4_HI | 16 Bit Unsigned Integer | calibrate value high byte input4
191 | 344 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL4_LO | 16 Bit Unsigned Integer | calibrate value low byte input4
192 | 345 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL5_HI | 16 Bit Unsigned Integer | calibrate value high byte input5
193 | 346 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL5_LO | 16 Bit Unsigned Integer | calibrate value low byte input5
194 | 347 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL6_HI | 16 Bit Unsigned Integer | calibrate value high byte input6
195 | 348 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL6_LO | 16 Bit Unsigned Integer | calibrate value low byte input6
196 | 349 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL7_HI | 16 Bit Unsigned Integer | calibrate value high byte input7
197 | 350 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL7_LO | 16 Bit Unsigned Integer | calibrate value low byte input7
198 | 351 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL8_HI | 16 Bit Unsigned Integer | calibrate value high byte input8
199 | 352 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL8_LO | 16 Bit Unsigned Integer | calibrate value low byte input8
200 | 353 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL9_HI | 16 Bit Unsigned Integer | calibrate value high byte input9
201 | 354 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL9_LO | 16 Bit Unsigned Integer | calibrate value low byte input9
202 | 355 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL10_HI | 16 Bit Unsigned Integer | calibrate value high byte input10
203 | 356 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL10_LO | 16 Bit Unsigned Integer | calibrate value low byte input10
204 | 357 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL11_HI | 16 Bit Unsigned Integer | calibrate value high byte input11
205 | 358 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL11_LO | 16 Bit Unsigned Integer | calibrate value low byte input11
206 | 359 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL12_HI | 16 Bit Unsigned Integer | calibrate value high byte input12
207 | 360 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL12_LO | 16 Bit Unsigned Integer | calibrate value low byte input12
208 | 361 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL13_HI | 16 Bit Unsigned Integer | calibrate value high byte input13
209 | 362 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL13_LO | 16 Bit Unsigned Integer | calibrate value low byte input13
210 | 363 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL14_HI | 16 Bit Unsigned Integer | calibrate value high byte input14
211 | 364 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL14_LO | 16 Bit Unsigned Integer | calibrate value low byte input14
212 | 365 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL15_HI | 16 Bit Unsigned Integer | calibrate value high byte input15
213 | 366 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL15_LO | 16 Bit Unsigned Integer | calibrate value low byte input15
214 | 367 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL16_HI | 16 Bit Unsigned Integer | calibrate value high byte input16
215 | 368 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL16_LO | 16 Bit Unsigned Integer | calibrate value low byte input16
216 | 369 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL17_HI | 16 Bit Unsigned Integer | calibrate value high byte input17
217 | 370 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL17_LO | 16 Bit Unsigned Integer | calibrate value low byte input17
218 | 371 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL18_HI | 16 Bit Unsigned Integer | calibrate value high byte input18
219 | 372 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL18_LO | 16 Bit Unsigned Integer | calibrate value low byte input18
220 | 373 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL19_HI | 16 Bit Unsigned Integer | calibrate value high byte input19
221 | 374 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL19_LO | 16 Bit Unsigned Integer | calibrate value low byte input19
222 | 375 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL20_HI | 16 Bit Unsigned Integer | calibrate value high byte input20
223 | 376 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL20_LO | 16 Bit Unsigned Integer | calibrate value low byte input20
224 | 377 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL21_HI | 16 Bit Unsigned Integer | calibrate value high byte input21
225 | 378 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL21_LO | 16 Bit Unsigned Integer | calibrate value low byte input21
226 | 379 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI0_STATUS | 8 Bit Unsigned Integer
227 | 380 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI1_STATUS | 8 Bit Unsigned Integer
228 | 381 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI2_STATUS | 8 Bit Unsigned Integer
229 | 382 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI3_STATUS | 8 Bit Unsigned Integer
230 | 383 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI4_STATUS | 8 Bit Unsigned Integer
231 | 384 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI5_STATUS | 8 Bit Unsigned Integer
232 | 385 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI6_STATUS | 8 Bit Unsigned Integer
233 | 386 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI7_STATUS | 8 Bit Unsigned Integer
234 | 387 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI8_STATUS | 8 Bit Unsigned Integer
235 | 388 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI9_STATUS | 8 Bit Unsigned Integer
236 | 389 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI10_STATUS | 8 Bit Unsigned Integer
237 | 390 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI11_STATUS | 8 Bit Unsigned Integer
238 | 391 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI12_STATUS | 8 Bit Unsigned Integer
239 | 392 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI13_STATUS | 8 Bit Unsigned Integer
240 | 393 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI14_STATUS | 8 Bit Unsigned Integer
241 | 394 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI15_STATUS | 8 Bit Unsigned Integer
242 | 395 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI16_STATUS | 8 Bit Unsigned Integer
243 | 396 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI17_STATUS | 8 Bit Unsigned Integer
244 | 397 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI18_STATUS | 8 Bit Unsigned Integer
245 | 398 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI19_STATUS | 8 Bit Unsigned Integer
246 | 399 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI20_STATUS | 8 Bit Unsigned Integer
247 | 400 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI21_STATUS | 8 Bit Unsigned Integer
248 | 401 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI22_STATUS | 8 Bit Unsigned Integer
249 | 800 | 03_06 Read Holding and Write Single | 1 | MODBUS_RESET | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset