## T38I8O6DO
ID | Register_Address | Operation | Register_Length | Register_Name | Data_Format | Description
1 | 0 | 03 Read Holding Registers (4x) | 4 | MODBUS_SERIALNUMBER | 32 Bit Unsigned Integer LO_HI | serial numbler
2 | 4 | 03 Read Holding Registers (4x) | 2 | MODBUS_FIRMWARE_VERSION | 16 Bit Unsigned Integer | firmware Version
3 | 6 | 03_06 Read Holding and Write Single | 1 | MODBUS_ADDRESS | 8 Bit Unsigned Integer | Modbus device address
4 | 7 | 03 Read Holding Registers (4x) | 1 | MODBUS_PRODUCT_MODEL | 16 Bit Unsigned Integer | Prodouct model
5 | 8 | 03 Read Holding Registers (4x) | 1 | MODBUS_HARDWARE_REV | 16 Bit Unsigned Integer | Hardware Version Number
6 | 30 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_DEAD_MASTER | 16 Bit Unsigned Integer | dead master of outputs
7 | 100 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE0 | 16 Bit Signed Integer | analog output1
8 | 101 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE1 | 16 Bit Signed Integer | analog output2
9 | 102 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE2 | 16 Bit Signed Integer | analog output3
10 | 103 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE3 | 16 Bit Signed Integer | analog output4
11 | 104 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE4 | 16 Bit Signed Integer | analog output5
12 | 105 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE5 | 16 Bit Signed Integer | analog output6
13 | 106 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE6 | 16 Bit Signed Integer | analog output7
14 | 107 | 03_06 Read Holding and Write Single | 1 | MODBUS_AO_CHANNLE7 | 16 Bit Signed Integer | analog output8
15 | 108 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE0 | 16 Bit Unsigned Integer | digit output1
16 | 109 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE1 | 16 Bit Unsigned Integer | digit output2
17 | 110 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE2 | 16 Bit Unsigned Integer | digit output3
18 | 111 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE3 | 16 Bit Unsigned Integer | digit output4
19 | 112 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE4 | 16 Bit Unsigned Integer | digit output5
20 | 113 | 03_06 Read Holding and Write Single | 1 | MODBUS_DO_CHANNLE5 | 16 Bit Unsigned Integer | digit output6
21 | 116 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE0 | Floating HI_LO/1000
22 | 118 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE1 | Floating HI_LO/1000
23 | 120 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE2 | Floating HI_LO/1000
24 | 122 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE3 | Floating HI_LO/1000
25 | 124 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE4 | Floating HI_LO/1000
26 | 126 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE5 | Floating HI_LO/1000
27 | 128 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE6 | Floating HI_LO/1000
28 | 130 | 03_06 Read Holding and Write Single | 2 | MODBUS_AI_CHANNLE7 | Floating HI_LO/1000
29 | 140 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP0 | 16 Bit Unsigned Integer | jumper setting for input0
30 | 141 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP1 | 16 Bit Unsigned Integer | jumper setting for input1
31 | 142 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP2 | 16 Bit Unsigned Integer | jumper setting for input2
32 | 143 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP3 | 16 Bit Unsigned Integer | jumper setting for input3
33 | 144 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP4 | 16 Bit Unsigned Integer | jumper setting for input4
34 | 145 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP5 | 16 Bit Unsigned Integer | jumper setting for input5
35 | 146 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP6 | 16 Bit Unsigned Integer | jumper setting for input6
36 | 147 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_CHANNEL_JUMP7 | 16 Bit Unsigned Integer | jumper setting for input7
37 | 149 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL0 | 16 Bit Unsigned Integer | auto manual setting for input0
38 | 150 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL1 | 16 Bit Unsigned Integer | auto manual setting for input1
39 | 151 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL2 | 16 Bit Unsigned Integer | auto manual setting for input2
40 | 152 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL3 | 16 Bit Unsigned Integer | auto manual setting for input3
41 | 153 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL4 | 16 Bit Unsigned Integer | auto manual setting for input4
42 | 154 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL5 | 16 Bit Unsigned Integer | auto manual setting for input5
43 | 155 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL6 | 16 Bit Unsigned Integer | auto manual setting for input6
44 | 156 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL7 | 16 Bit Unsigned Integer | auto manual setting for input7
45 | 157 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI0 | 16 Bit Unsigned Integer | digit and analog setting for input0
46 | 158 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI1 | 16 Bit Unsigned Integer | digit and analog setting for input1
47 | 159 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI2 | 16 Bit Unsigned Integer | digit and analog setting for input2
48 | 160 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI3 | 16 Bit Unsigned Integer | digit and analog setting for input3
49 | 161 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI4 | 16 Bit Unsigned Integer | digit and analog setting for input4
50 | 162 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI5 | 16 Bit Unsigned Integer | digit and analog setting for input5
51 | 163 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI6 | 16 Bit Unsigned Integer | digit and analog setting for input6
52 | 164 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_DI_AI7 | 16 Bit Unsigned Integer | digit and analog setting for input7
53 | 165 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN0 | 16 Bit Unsigned Integer | calibrate sign for input0
54 | 166 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN1 | 16 Bit Unsigned Integer | calibrate sign for input1
55 | 167 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN2 | 16 Bit Unsigned Integer | calibrate sign for input2
56 | 168 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN3 | 16 Bit Unsigned Integer | calibrate sign for input3
57 | 169 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN4 | 16 Bit Unsigned Integer | calibrate sign for input4
58 | 170 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN5 | 16 Bit Unsigned Integer | calibrate sign for input5
59 | 171 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN6 | 16 Bit Unsigned Integer | calibrate sign for input6
60 | 172 | 03_06 Read Holding and Write Single | 1 | MODBUS_CAL_SIGN7 | 16 Bit Unsigned Integer | calibrate sign for input7
61 | 173 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE0 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input0
62 | 175 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE1 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input1
63 | 177 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE2 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input2
64 | 179 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE3 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input3
65 | 181 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE4 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input4
66 | 183 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE5 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input5
67 | 185 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE6 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input6
68 | 187 | 03_06 Read Holding and Write Single | 2 | MODBUS_CAL_VALUE7 | 32 Bit Unsigned Integer HI_LO | calibrate value which has high byte and low byte for input7
69 | 189 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_0 | 16 Bit Unsigned Integer | status for input0
70 | 190 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_1 | 16 Bit Unsigned Integer | status for input1
71 | 191 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_2 | 16 Bit Unsigned Integer | status for input2
72 | 192 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_3 | 16 Bit Unsigned Integer | status for input3
73 | 193 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_4 | 16 Bit Unsigned Integer | status for input4
74 | 194 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_5 | 16 Bit Unsigned Integer | status for input5
75 | 195 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_6 | 16 Bit Unsigned Integer | status for input6
76 | 196 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_STATUS_7 | 16 Bit Unsigned Integer | status for input7
77 | 200 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER0 | 16 Bit Unsigned Integer | filter value for input0
78 | 201 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER1 | 16 Bit Unsigned Integer | filter value for input1
79 | 202 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER2 | 16 Bit Unsigned Integer | filter value for input2
80 | 203 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER3 | 16 Bit Unsigned Integer | filter value for input3
81 | 204 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER4 | 16 Bit Unsigned Integer | filter value for input4
82 | 205 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER5 | 16 Bit Unsigned Integer | filter value for input5
83 | 206 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER6 | 16 Bit Unsigned Integer | filter value for input6
84 | 207 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_FILTER7 | 16 Bit Unsigned Integer | filter value for input7
85 | 225 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE0 | 16 Bit Unsigned Integer | analog input 0 range. if analog inputs (not_used_input = 0, Y3K_40_150DegC = 1, Y3K_40_300DegF, R10K_40_120DegC, R10K_40_250DegF, R3K_40_150DegC, R3K_40_300DegF, KM10K_40_120DegC, KM10K_40_250DegF, A10K_50_110DegC, A10K_60_200DegF, V0_5, I0_100Amps, I0
86 | 226 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE1 | 16 Bit Unsigned Integer | range value for input1
87 | 227 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE2 | 16 Bit Unsigned Integer | range value for input2
88 | 228 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE3 | 16 Bit Unsigned Integer | range value for input3
89 | 229 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE4 | 16 Bit Unsigned Integer | range value for input4
90 | 230 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE5 | 16 Bit Unsigned Integer | range value for input5
91 | 231 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE6 | 16 Bit Unsigned Integer | range value for input6
92 | 232 | 03_06 Read Holding and Write Single | 1 | MODBUS_AI_RANGE7 | 16 Bit Unsigned Integer | range value for input7
93 | 240 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT0 | 16 Bit Unsigned Integer | auto manual setting for output0
94 | 241 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT1 | 16 Bit Unsigned Integer | auto manual setting for output1
95 | 242 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT2 | 16 Bit Unsigned Integer | auto manual setting for output2
96 | 243 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT3 | 16 Bit Unsigned Integer | auto manual setting for output3
97 | 244 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT4 | 16 Bit Unsigned Integer | auto manual setting for output4
98 | 245 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT5 | 16 Bit Unsigned Integer | auto manual setting for output5
99 | 246 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT6 | 16 Bit Unsigned Integer | auto manual setting for output6
100 | 247 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT7 | 16 Bit Unsigned Integer | auto manual setting for output7
101 | 248 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT8 | 16 Bit Unsigned Integer | auto manual setting for output8
102 | 249 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT9 | 16 Bit Unsigned Integer | auto manual setting for output9
103 | 250 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT10 | 16 Bit Unsigned Integer | auto manual setting for output10
104 | 251 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT11 | 16 Bit Unsigned Integer | auto manual setting for output11
105 | 252 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT12 | 16 Bit Unsigned Integer | auto manual setting for output12
106 | 253 | 03_06 Read Holding and Write Single | 1 | MODBUS_AUTO_MANUAL_OUT13 | 16 Bit Unsigned Integer | auto manual setting for output13
107 | 254 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_0 | 16 Bit Unsigned Integer | status for outputs0
108 | 255 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_1 | 16 Bit Unsigned Integer | status for outputs1
109 | 256 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_2 | 16 Bit Unsigned Integer | status for outputs2
110 | 257 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_3 | 16 Bit Unsigned Integer | status for outputs3
111 | 258 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_4 | 16 Bit Unsigned Integer | status for outputs4
112 | 259 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_5 | 16 Bit Unsigned Integer | status for outputs5
113 | 260 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_6 | 16 Bit Unsigned Integer | status for outputs6
114 | 261 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_7 | 16 Bit Unsigned Integer | status for outputs7
115 | 262 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_8 | 16 Bit Unsigned Integer | status for outputs8
116 | 263 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_9 | 16 Bit Unsigned Integer | status for outputs9
117 | 264 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_10 | 16 Bit Unsigned Integer | status for outputs10
118 | 265 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_11 | 16 Bit Unsigned Integer | status for outputs11
119 | 266 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_12 | 16 Bit Unsigned Integer | status for outputs12
120 | 267 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_STATUS_13 | 16 Bit Unsigned Integer | status for outputs13
121 | 268 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_0 | 16 Bit Unsigned Integer | high bye is analog or digital (digital is 0, analog is 1), low byte is range. if analog inputs (not_used_input = 0, Y3K_40_150DegC, Y3K_40_300DegF, R10K_40_120De
122 | 269 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_1 | 16 Bit Unsigned Integer
123 | 270 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_2 | 16 Bit Unsigned Integer
124 | 271 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_3 | 16 Bit Unsigned Integer
125 | 272 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_4 | 16 Bit Unsigned Integer
126 | 273 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_5 | 16 Bit Unsigned Integer
127 | 274 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_6 | 16 Bit Unsigned Integer
128 | 275 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_7 | 16 Bit Unsigned Integer
129 | 276 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_8 | 16 Bit Unsigned Integer
130 | 277 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_9 | 16 Bit Unsigned Integer
131 | 278 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_10 | 16 Bit Unsigned Integer
132 | 279 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_11 | 16 Bit Unsigned Integer
133 | 280 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_12 | 16 Bit Unsigned Integer
134 | 281 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RANGE_13 | 16 Bit Unsigned Integer
135 | 282 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH1 | 16 Bit Unsigned Integer | 0 - OFF, 1 - HAND, 2 - AUTO
136 | 283 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH2 | 16 Bit Unsigned Integer
137 | 284 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH3 | 16 Bit Unsigned Integer
138 | 285 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH4 | 16 Bit Unsigned Integer
139 | 286 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH5 | 16 Bit Unsigned Integer
140 | 287 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH6 | 16 Bit Unsigned Integer
141 | 288 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH7 | 16 Bit Unsigned Integer
142 | 289 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH8 | 16 Bit Unsigned Integer
143 | 290 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH9 | 16 Bit Unsigned Integer
144 | 291 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH10 | 16 Bit Unsigned Integer
145 | 292 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH11 | 16 Bit Unsigned Integer
146 | 293 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH12 | 16 Bit Unsigned Integer
147 | 294 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH13 | 16 Bit Unsigned Integer
148 | 295 | 03 Read Holding Registers (4x) | 1 | MODBUS_OUTPUT_SWITCH14 | 16 Bit Unsigned Integer
149 | 342 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD0 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 0
150 | 343 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD1 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 1
151 | 344 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD2 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 2
152 | 345 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD3 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 3
153 | 346 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD4 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 4
154 | 347 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD5 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 5
155 | 348 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD6 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 6
156 | 349 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD7 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 7
157 | 350 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD8 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 8
158 | 351 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD9 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 9
159 | 352 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD10 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 10
160 | 353 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD11 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 11
161 | 354 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD12 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 12
162 | 355 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_AD13 | 16 Bit Unsigned Integer | analog or digital (0 is digtal output, 1 is analog output) for output 13
163 | 800 | 03_06 Read Holding and Write Single | 1 | MODBUS_RESET | 16 Bit Unsigned Integer | 1-> reset to factory, other -> reset
164 | 9400 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_1 | Floating HI_LO/1000 | high word of output1 relinquish
165 | 9401 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_1 | Floating HI_LO/1000 | low word of output1 relinquish
166 | 9402 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_2 | Floating HI_LO/1000 | high word of output2 relinquish
167 | 9403 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_2 | Floating HI_LO/1000 | low word of output2 relinquish
168 | 9404 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_3 | Floating HI_LO/1000 | high word of output3 relinquish
169 | 9405 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_3 | Floating HI_LO/1000 | low word of output3 relinquish
170 | 9406 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_4 | Floating HI_LO/1000 | high word of output4 relinquish
171 | 9407 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_4 | Floating HI_LO/1000 | low word of output4 relinquish
172 | 9408 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_5 | Floating HI_LO/1000 | high word of output5 relinquish
173 | 9409 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_5 | Floating HI_LO/1000 | low word of output5 relinquish
174 | 9410 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_6 | Floating HI_LO/1000 | high word of output6 relinquish
175 | 9411 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_6 | Floating HI_LO/1000 | low word of output6 relinquish
176 | 9412 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_7 | Floating HI_LO/1000 | high word of output7 relinquish
177 | 9413 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_7 | Floating HI_LO/1000 | low word of output7 relinquish
178 | 9414 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_8 | Floating HI_LO/1000 | high word of output8 relinquish
179 | 9415 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_8 | Floating HI_LO/1000 | low word of output8 relinquish
180 | 9416 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_9 | Floating HI_LO/1000 | high word of output9 relinquish
181 | 9417 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_9 | Floating HI_LO/1000 | low word of output9 relinquish
182 | 9418 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_10 | Floating HI_LO/1000 | high word of output10 relinquish
183 | 9419 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_10 | Floating HI_LO/1000 | low word of output10 relinquish
184 | 9420 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_11 | Floating HI_LO/1000 | high word of output11 relinquish
185 | 9421 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_11 | Floating HI_LO/1000 | low word of output11 relinquish
186 | 9422 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_12 | Floating HI_LO/1000 | high word of output12 relinquish
187 | 9423 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_12 | Floating HI_LO/1000 | low word of output12 relinquish
188 | 9424 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_13 | Floating HI_LO/1000 | high word of output13 relinquish
189 | 9425 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_13 | Floating HI_LO/1000 | low word of output13 relinquish
190 | 9426 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_HI_14 | Floating HI_LO/1000 | high word of output14 relinquish
191 | 9427 | 03_06 Read Holding and Write Single | 1 | MODBUS_OUTPUT_RELINQUISH_LO_14 | Floating HI_LO/1000 | low word of output14 relinquish